**TECHNICAL SPECIFICATIONS : VAPOUR ABSORPTION CHILLER**

|  |  |  |  |
| --- | --- | --- | --- |
| Client | a | Version | 1.2.0 Dt : 07-Aug-2021 |
| Enquiry | a | Date | 20-Sep-2021, 13:22 |
| Project | a | Model | TAC E2 M1 |

|  |  |  |  |
| --- | --- | --- | --- |
|  | **Description** | **Unit** |  |
|  | **Capacity ( + 3 %) :** | **TR** | 40 |
|  | | | |
| **A** | **Chilled Water Circuit :** | | |
|  | Chilled water flow | m³/hr | 24.1 |
|  | Chilled water inlet temperature | °C | 12 |
|  | Chilled water outlet temperature | °C | 7 |
|  | Evaporate passes | No. | 2+2 |
|  | Chilled water circuit pressure loss | mLC | 5.3 |
|  | Chilled water Connection diameter | DN | 80 |
|  | Glycol type |  | NA |
|  | Chilled water glycol % | % | 0 |
|  | Chilled water fouling factor | m² hr °C/kcal | standard |
|  | Maximum working pressure | kg/cm²(g) | 8 |
|  | | | |
| **B** | **Cooling Water Circuit:** | | |
|  | Heat Rejected | kCal/hr | 204485.7 |
|  | Cooling water flow | m³/hr | 48 |
|  | Cooling water inlet temperature | °C | 32 |
|  | Cooling water outlet temperature | °C | 36.3 |
|  | Absorber / Condenser passes | No. | 1+1/2 |
|  | Cooling water Bypass Flow | m³/hr | - |
|  | Cooling water circuit pressure loss | mLC | 5 |
|  | Cooling water Connection diameter | DN | 100 |
|  | Glycol type |  | NA |
|  | Cooling water glycol % | % | 0 |
|  | Cooling water fouling factor | m² hr °C/kcal | standard |
|  | Maximum working pressure | kg/cm²(g) | 8 |
|  | | | |
| **C** | **EXHAUST GAS CIRCUIT :** | | |
| 1. | Heat Input | kCal/hr | 83525.7 |
| 2. | Engine Type | - | gas |
| 3. | Exhaust Gas Flow (+/-3%) | kg/hr | 1300 |
| 4. | Exhaust Gas inlet temperature | °C | 500 |
| 5. | Exhaust Gas Outlet temperature | °C | 257.5 |
| 6. | Exhaust Connection Diameter(Indicative) | DN | 250 |
| 7. | Exhaust Gas Sp.Heat Capacity | kcal/kg°C | 0.273 |
| 8. | Exhaust Gas Flow | kg/hr | 1300 |
| 9. | Percentage Engine Load considered | % | 99 |
| 10. | Allowable Pressure Drop in VAM - EG Furnace | mmWC | 150 |
|  | | | |
| **D** | **Electrical Data :** | | |
| 1. | Power supply |  | 415 V( ±10%), 50 Hz (±5%), 3 Phase+N |
| 2. | Power consumption | kVA | 5.5 |
| 3. | Absorbent pump rating | kW (A) | 1.1 (3.4) |
| 4. | Refrigerant pump rating | kW (A) | 0.2 (1.1) |
| 5. | Vacuum pump rating | kW (A) | 0.75 (1.8) |
|  | | | |
| **F** | **Tube Metallurgy :** | | |
| 1. | Evaporator |  | name |
| 2. | Absorber tube material |  | Copper |
| 3. | Condenser tube material |  | Copper |
|  | | | |

Caption Notes:

1. This selection is valid for insulated chiller only.

2. For non-insulated chiller, the Capacity and Heat source consumption will vary.

3. Plant Room Temperature should be from +5 deg C to +45 deg C

4. Please contact Thermax representative / Office for customised specifications.